**Water Shortage Response Plan**

**Town of Clarkton, North Carolina**

**April 20, 2023**

The procedures herein are written to reduce potable water demand and supplement existing drinking water supplies whenever existing water supply sources are inadequate to meet current demands for potable water.

**I. Authorization**

The Clarkton Town’s Mayor shall enact the following water shortage response provisions whenever the trigger conditions outlined in Section IV are met. In their absence, the Public Works Director will assume this role.

Mr. Tim Tart Daniel Alonzo

Mayor Clarkton Public Utilities

Phone: 910-647-5961 Phone: 910-647-5961

**II. Notification**

The following notification methods will be used to inform water system employees and customers of a water shortage declaration: employee e-mail announcements, notices at municipal buildings, Post Office, notices in water bills. Required water shortage response measures will be communicated to all customers by either a mailed or hand delivered notice.

**III. Levels of Response**

Five levels of water shortage response are outlined in the table below. The five levels of water shortage response are: voluntary reductions, mandatory reductions I and II, emergency reductions and water rationing. A detailed description of each response level and corresponding water reduction measures follow below.

|  |  |  |
| --- | --- | --- |
| Stage Response Description | | |
|  | Voluntary  Reductions | Water users are encouraged to reduce their water use and improve water use efficiency; however, no penalties apply for noncompliance. Water supply conditions indicate a potential for shortage. |
|  | Mandatory  Reductions I | Water users must abide required water use reduction and efficiency measures; penalties apply for noncompliance. Water supply conditions are significantly lower than the seasonal norm and water shortage conditions are expected to persist. |
|  | Mandatory  Reductions II | Same as in Stage 2 |
|  | Emergency  Reductions | Water supply conditions are substantially diminished and pose an imminent threat to human health or environmental integrity. |
|  | Water  Rationing | Water supply conditions are substantially diminished, and remaining supplies must be allocated to preserve human health and environmental integrity. |

*In Stage 1*, Voluntary Reductions, all water users will be asked to reduce their normal water use by 5%. Customer education and outreach programs will encourage water conservation and efficiency measures including: irrigating landscapes a maximum of one inch per week; preventing water waste, runoff and watering impervious surfaces; watering plants deeply to encourage root growth; washing only full loads in clothes and

dishwashers; using spring-loaded nozzles on garden hoses; and identifying and repairing all water leaks.

*In Stage 2*, Mandatory Reductions I, all customers are expected to reduce their water use by 10% in comparison to their previous month’s water bill. In addition to continuing to encourage all voluntary reduction actions, the following restrictions apply: irrigation is limited to a half inch per week between 8PM and 8AM; outdoor use of drinking water for washing impervious surfaces is prohibited; and all testing and training purposes requiring drinking water (e.g. fire protection) will be limited.

*In Stage 3*, Mandatory Reductions II, customers must continue actions from all previous stages and further reduce water use by 20% compared to their previous month’s water bill. All non-essential uses of drinking water are banned, and garden and landscape irrigation must be reduced to the minimum amount necessary for survival. Additionally, in Stage 3, a drought surcharge of 1.5 times the normal water rate applies.

*In Stage 4*, Emergency Reductions, customers must continue all actions from previous stages and further reduce their water use by 25% compared to their previous month’s water bill. A ban on all use of drinking water except to protect public health and safety is implemented and drought surcharges increase to 2 times the normal water rate.

The goal of *Stage 5*, Water Rationing, is to provide drinking water to protect public health (e.g. residences, residential health care facilities and correctional facilities). In Stage 5, all customers are only permitted to use water at the minimum required for public health protection. Firefighting is the only allowable outdoor water use and pickup locations for distributing potable water will be announced according to Clarkton’s Emergency Response Plan. Drought surcharges increase to 5 times the normal water rate.

**IV. Triggers**

The Town of Clarkton’s water source is ground water. The following measurements of well pumping times and well levels in relationship to pump intake levels shall trigger any into the corresponding water restrictions stage.

|  |  |  |
| --- | --- | --- |
| Stage Description | | |
| 1 | Pumping time > 10 hrs  20% reduction in seasonal normal distance from static water level and pump intake  20% increase pumping time for same output |
| 2 | Pumping time > 12 hrs  40% reduction in seasonal normal distance from static w6ter level and pump intake  40% increase pumping time for same output |
| 3 | Pumping time > 14 hrs  60% reduction in seasonal normal distance from static water level and pump intake  40% increase pumping time for same output |
| 4 | Pumping time > 20 hrs  80% reduction in seasonal normal distance from static water level and pump intake |
| 5 | Water level at pump intake |

Return to Normal

When water shortage conditions have abated and the situation is returning to normal, water conservation measures employed during each phase should be decreased in reverse order of implementation. Permanent measures directed toward long-term monitoring and conservation should be implemented or continued so that the community will be in a better position to prevent shortages and respond to recurring water shortage conditions.

**V. Enforcement**

The provisions of the water shortage response plan will be enforced by Town of Clarkton Public Works personnel and local law enforcement. Violators may be reported to the Town’s phone line. Citations are assessed according to the following schedule depending on the number of prior violations and current level of water shortage.

|  |  |  |  |
| --- | --- | --- | --- |
| **Water Shortage Level** | **First Violation** | **Second Violation** | **Third Violation** |
| Voluntary Reductions | N/A | N/A | N/A |
| Mandatory Reductions  (Stages 2 and 3) | Warning | $250 | Discontinuation of  Service |
| Emergency Reductions | $250 | Discontinuation of  Service | Discontinuation of  Service |
| Water Rationing | $500 | Discontinuation of  Service | Discontinuation of  Service |

Drought surcharge rates are effective in Stages 3, 4 and 5.

**VI. Public Comment**

Customers will have multiple opportunities to comment on the provisions of the water shortage response plan. A copy of this plan will be posted at the Town Hall for the public. All comments can be given to the Town Clerk in written or verbal comments. Any revisions will be in accordance with Section IX as noted below.

**VII. Variance Protocols**

Applications for water use variance requests are available from the Town Hall. All applications must be submitted to the Town Hall for review by the Utility Officer for review by the Public Utilities Director of their designee. A decision to approve or deny individual variance requests will be determined within two weeks of submittal after careful consideration of the following criteria: impact on water demand, expected duration, alternative source options, social and economic importance, purpose (i.e. necessary use of drinking water) and the prevention of structural damage.

**VIII. Effectiveness**

The effectiveness of the Clarkton water shortage response plan will be determined by comparing the stated water conservation goals with observed water use reduction data. Other factors to be considered include frequency of plan activation, any problem periods without activation, total number of violation citations, desired reductions attained, and evaluation of demand reductions compared to the previous year’s seasonal data.

**IX. Revision**

The water shortage response plan will be reviewed and revised as needed to adapt to new circumstances affecting water supply and demand, following implementation of emergency restrictions, and at a minimum of every five years in conjunction with the updating of our Local Water Supply Plan. Further, a water shortage response planning work group will review procedures following each emergency or rationing stage to recommend any necessary improvements to the plan to Clarkton’s Town Council. The Town of Clarkton Public Utilities Director is responsible for initiating all subsequent revisions.